Installation

Fiber Optic

Cables

By

Mohd Nasir bin Said

Telecommunications Department

Advanced Technology Training Centre

Kulim Kedah Darul Aman

# Pulling Fiber Optic Cables

### 1) Planning the Run:

1a) Underground Conduits: We recommend that underground conduits, if newly installed, should be a minimum size of between 1.5" to 2". If the run is long, or if you anticipate the possibility of additional future pulls; Then you may want to install a conduit of up to 4" (or greater). Once the trench is dug, the installation of the conduit is comparably easy and inexpensive. You may also want to consider installing additional conduits for future use. 

1b) Conduit Installations General Information:

- Try to design the conduit run with a few bends as possible. If there are too many bends in the run then you may consider installing junction boxes in lieu of bends. Note: There is some controversy on installing junction boxes in lieu of bends. Read more information.

- Use plastic bushings on conduit ends to avoid damage to the cable during the pull.

1c) In Buildings: It is not necessary to pull fiber optic cable in innerduct. Innerduct is strictly a personal preference. The following instruction takes into consideration that you will pull the fiber optic cable directly into the ceiling or other space. Plan for straight pulls only (point A to point B). Diagonal pulling across an area will be OK but it would make for a neater and more professional installation to install the cable at an angle that is parallel to a wall. Do not attempt to pull the cable around a corner, even if you plan on having a person feeding it from hand to hand around the corner. Instead, pull all of the cable out (at the turn) and lay it on the floor in a figure 8 pattern (See Installing - item #2e below).

### 2) Installing the cable:

2a) Rope Size: It is important to use a rope size that give minimal stretching during the pull. Stretching of the rope is undesirable for several reasons including that it makes for a very unstable pull, and takes away control from those doing the pulling. This is why we do not recommend using 200 lb. pull string (aka: jetline) to pull the cable. We recommend a heavier rope that is anywhere from a 1/4" to 1/2" in thickness. The thickness of the rope should increase with greater pull lengths. Have the pull rope installed before the cable pulling crew arrives for maximum efficiency. 

2b) Communication between the person feeding and the person pulling the cable is absolutely essential. If the person feeding runs into a snag then the puller must stop immediately to avoid damage to the cable. Walkie-talkies would come in handy for this purpose. Use of great pulling force is not recommended and will likely damage the terminations and/or the cable. 

2c) Use a generous amount of cable pulling lubricant on the entire run, especially on the leader (pulling eye & mesh). The person may stop the cable pull from time to time to prepare and apply more lubricant. Use only lubricant that is expressly designed for cable pulling. When working in freezing temperatures, use a lubricant that is designed not to freeze. 

2d) Do make every effort to pull cables from a conduit in as straight an angle as possible. Pulling on an angle can cause damage to the cable.

2e) How to Handle Slack: When pulling cable out from a conduit or ceiling, it will become necessary to coil up the cable in preparation to pull it in another direction. Fiber Optic cable has a "memory". That is to say that it holds it's contour that it formed while being on a reel. Do not try to re-coil the cable in a circular pattern; Instead use a figure - 8 pattern as shown in the illustration. When you are finished pulling out all of the slack, turn the figure - 8 cable 360Â°n(upside down) and proceed to setup to pull it in the other direction.

2f) Removing the Pull Eye: Use extreme caution when removing the pull eye. Do not use a blade to slit the mesh. Instead, use a pair of electricians scissors or diagonal cutters. Work your way from the back of the cable toward the pull eye, while lifting the mesh upward, away from the cable. 

2g) Follow Building Codes: Always obey all local, and national, fire and building codes. Be sure to "firestop" all cables that penetrate a firewall. Use plenum rated cable where it is mandated, etc., etc.

### Pre-Terminated Fiber Optic Cable Assemblies

These factory pre-terminated fiber-optic cable assemblies (aka: "Ready Pull") have received rave reviews from our customers . The assemblies can be ordered in either indoor (plenum) or outdoor versions, and in 4, 6, 12 or 24 strand fiber counts, and in multimode or Singlemode! A pulling eye can be factory installed on either end or on both ends of the cable. The pulling eye (and associated cable netting) will protect the pre-terminated ends during the pull. This product is a great time and money saver for those who occasionally install fiber optic cabling.

### Important Ordering Information

#### 1) Cable Jacket Types

Indoor (Plenum): The cable is rated for all indoor installations, including plenum rated spaces. A cable rated for plenum installation will have low-smoke characteristics as defined by the NFPA (National Fire Protection Agency). 

Outdoor: Outdoor cables are filled with a water blocking jell and are rated for all outdoor applications except for "direct bury". This cable is suitable for underground installation in conduit, overhead lashed to a guy wire, or secured to a building or other permanent outdoor structure. The drawback of the jell-filled cable is that it is mandated at a maximum of 50 feet run indoors due to fire-code regulations. Please note that the only difference between outdoor (jell-filled) and direct bury cable is that the latter has an added overall metallic sheath which gives it protection from rodents. If you require a direct bury cable, please contact sales for a quote. 

Indoor/Outdoor: Indoor/Outdoor cables are approved for use in underground conduits, even if the possibility of water infiltration exists. Indoor/Outdoor cables are not recommended for aerial installations. The advantage of using Indoor/Outdoor over standard Outdoor cable is that it does not have the 50 foot restriction for indoor installation that standard outdoor cable has. This cable has an overall PVC sheath and is not rated for plenum spaces.

#### 2) Running Through Different Environments

Say for example that you have a cable run that will go from building A to building B. In building A, there is a 100 foot run through a plenum space. Then the cable must run overhead from pole to pole for a distance of 550 feet to building B. In building B, the cable must be run for a distance of 150 feet through a plenum space. Obviously, this cannot be done with a single cable. The way to do this is with three separate cables. The pre-terminated cables can be joined together in buildings A & B by the use of Fiber Optic Distribution boxes. See diagram below:

#### 3) How To Take An Accurate Measurement

It is extremely important to take an accurate measurement when planning an order for a custom pre-terminated fiber optic cable assembly. These custom assemblies cannot be returned unless out of box defective. 

We recommend that you fish through a small (200 lb. rated) polypropylene pull string from end to end (termination point to termination point). The string should follow the exact path and be shaped to the run in the exact way that the final cable will be installed, from end to end. At each termination end, shape the string over to the termination point and add at least 15 feet and cut the string. Once this has been done on both ends the string should be removed. You may want to replace the string with a heavier rope for later pulling of the cable (see installation recommendations item #2 below). Once the string is removed, take an accurate measurement and record it. It is always better to have a cable that is longer than shorter for obvious reasons. Slack coils of the cable may be put by each termination point.

#### 4) Pulling Eye Recommendations

Optional pulling eyes are highly recommended. The pulling eye pulling eye (and associated cable netting) will protect the pre-terminated ends during the pull. In many cases, pulling is not done from point to point, but rather from an intermediate point pulling back in each direction to each termination location. In that scenario, you will need to order the cable with two pulling eyes. In many cases, a cable run is planned to pull direct from point to point. When the installation begins, occasionally, the decision is made to pull from an intermediate point rather than from point to point (in which case you'll be glad that you ordered the extra pulling eye).

# Fiber Optic Network

In the telcos, singlemode fiber is used to connect long distance switches, central offices and SLCs (subscriber loop carriers, small switches in pedestals in subdivisions or office parks or in the basement of a larger building). Practically every telco's network is now fiber optics except the connection to the home. Fiber to the home is not yet cost effective - especially since most homes do not want (nor are willing to pay) for the high speed services that would justify fiber optics. 

CATV companies "overbuild" with fiber. They lash fiber cable onto the aerial "hardline" coax used for the rest of the network or pull it in the same conduit underground. The fiber allows them to break their network into smaller service areas that prevent large numbers of customers from being affected in an outage, making for better service and customer relations. The fiber also gives them a return path which they use for Internet and telephone connections, increasing their revenue potential. 

LANs (local area networks) use fiber optics primarily in the backbone but increasingly to the desk. The LAN backbone often needs longer distance than copper cable (Cat 5/5e/6) can provide and of course, the fiber offers higher bandwidth for future expansion. Most large corporate LANs use fiber backbones with copper wire to the desktop. Fiber to the desk can be cost effective if properly designed. 

Lots of other networks use fiber. CCTV is often on fiber for it's distance capability. Industrial plants use lots of fiber or distance and noise immunity. Utilities use it for network management, liking its immunity to noise also. The military uses it because it's hard to tap or jam. Airplanes use it for that reason too, but also like the lighter weight of fiber.

### Designing Cable Networks

I guess this is too big a topic for a overview! But we'll pass along some hints to make life easier. First and foremost, visit the work site and check it out thoroughly. Know the "standards" but use common sense in designing the installation. Don't cut corners which may affect performance or reliability. Consider what are the possible problems and work around or prevent them. There ain't no substitute for common sense here! 

Fiber's extra distance capability makes it possible to do things not possible with copper wire. For example, you can install all the electronics for a network in one communications closet for a building and run straight to the desktop with fiber. With copper, you can only go about 90 meters (less than 300 feet), so you need to keep the electronics close to the desk. With fiber, you only need passive patch panels locally to allow for moves. Upgrades are easy, since the fiber is only loafing at today's network speed!

### Is Copper Really Cheaper Than Fiber?

When it comes to costs, fiber optics is always assumed to be much more expensive than copper cabling. Whatever you look at - cable, terminations or networking electronics - fiber costs more, although as copper gets faster (e.g. Cat 6) it gets more expensive, almost as much as fiber. So isn't it obvious that fiber networks are more expensive than copper? Maybe not! There is more to consider in making the decision.

### Why Use Fiber?

If fiber is more expensive, why have all the telephone networks been converted to fiber? And why are all the CATV systems converting to fiber too? Are their networks that different? Is there something they know we don't? Telcos use fiber to connect all their central offices and long distance switches because it has thousands of times the bandwidth of copper wire and can carry signals hundreds of times further before needing a repeater. The CATV companies use fiber because it give them greater reliability and the opportunity to offer new services, like phone service and Internet connections. Both telcos and CATV operators use fiber for economic reasons, but their cost justification requires adopting new network architectures to take advantage of fiber's strengths. A properly designed premises cabling network can also be less expensive when done in fiber instead of copper. There are several good examples of fiber being less expensive, so lets examine them.

### Industrial Networks

In an industrial environment, electromagnetic interference (EMI) is often a big problem. Motors, relays, welders and other industrial equipment generate a tremendous amount of electrical noise that can cause major problems with copper cabling, especially unshielded cable like Cat 5. In order to run copper cable in an industrial environment, it is often necessary to pull it through conduit to provide adequate shielding. With fiber optics, you have complete immunity to EMI. You only need to choose a cable type that is rugged enough for the installation, with breakout cable being a good choice for it's heavy-duty construction. The fiber optic cable can be installed easily from point to point, passing right next to major sources of EMI with no effect. Conversion from copper networks is easy with media converters, gadgets that convert most types of systems to fiber optics. Even with the cost of the media converters, the fiber optic network will be less than copper run in conduit.

### Long Cable Runs

Most networks are designed around structured cabling installed per EIA/TIA 568 standards. This standard calls for 90 meters (295 feet) of permanently installed unshielded twisted pair (UTP) cable and 10 meters (33 feet) of patchcords. But suppose you need to connect two buildings or more? The distance often exceeds the 90 meters by the time you include the runs between the buildings plus what you need inside each building. By the time you buy special aerial or underground waterproof copper cable and repeaters, you will usually spend more than if you bought some outside plant fiber optic cable and a couple of inexpensive media converters. It's guaranteed cheaper if you go more than two links (180 meters.)

### Centralized Fiber LANs

When most contractors and end users look at fiber optics versus Cat 5e cabling for a LAN, they compare the same old copper LAN with fiber directly replacing the copper links. The fiber optic cable is a bit more expensive than Cat 5e and terminations are a little more too, but the big difference is the electronics which are $200 or more per link extra for fiber. However, the real difference comes if you use a centralized fiber optic network - shown on the right of the diagram above. Since fiber does not have the 90 meter distance limitation of UTP cable, you can place all electronics in one location in or near the computer room. The telecom closet is only used for passive connection of backbone fiber optic cables, so no power, UPS, ground or air conditioning is needed. These auxiliary services, necessary with Cat 5 hubs, cost a tremendous amount of money in each closet. In addition, having all the fiber optic hubs in one location means better utilization of the hardware, with fewer unused ports. Since ports in modular hubs must be added in modules of 8 or 16, it's not uncommon with a hub in a telecom closet to have many of the ports in a module empty . With a centralized fiber system, you can add modules more efficiently as you are supporting many more desktop locations but need never have more than a one module with open ports.

### High Speed Networking

It was over a year after Gigabit Ethernet (GbE) became available on fiber optics that it finally become available on Cat 5e. It took another couple of years before GbE on copper became significantly less expensive. In order to get GbE to work over Cat 5e, the electronics must be very complicated, and consequently as expensive as fiber. A newer version is in the wings, awaiting a Cat 6 standard, but that means the version running over Cat 5e will be obsolete before it even gets started! Finally, we went to a major distributor's seminar on advanced cabling recently and the copper marketing guy told us to go fiber for GbE.

### Bottom Line

So when it comes to costs, looking at the cabling component costs may not be a good way to analyze total network costs. Consider the total system and you may find fiber looks a lot more attractive.

Testing

Fiber Optic

Cables

By

Mohd Nasir bin Said

Telecommunications Department

Advanced Technology Training Centre

Kulim Kedah Darul Aman

# Fiber Optic Testing

After the cables are installed and terminated, it's time for testing. For every fiber optic cable plant, you will need to test for continuity, end-to-end loss and then troubleshoot the problems. If it's a long outside plant cable with intermediate splices, you will probably want to verify the individual splices with an OTDR also, since that's the only way to make sure that each one is good. If you are the network user, you will also be interested in testing power, as power is the measurement that tells you whether the system is operating properly. 

You'll need a few special tools and instruments to test fiber optics. See Jargon in the beginning of Lennie's Guide to see a description of each instrument.

### Getting Started

Even if you're an experienced installer, make sure you remember these things.

#### 1. Have the right tools and test equipment for the job. You will need:

1. Source and power meter, optical loss test set or test kit with proper equipment adapters for the cable plant you are testing.
2. Reference test cables that match the cables to be tested and mating adapters, including hybrids if needed.
3. Fiber Tracer or Visual Fault Locator.
4. Cleaning materials - lint free cleaning wipes and pure alcohol.
5. OTDR and launch cable for outside plant jobs.

#### 2. Know how to use your test equipment

Before you start, get together all your tools and make sure they are all working properly and you and your installers know how to use them. It's hard to get the job done when you have to call the manufacturer from the job site on your cell phone to ask for help. Try all your equipment in the office before you take it into the field. Use it to test every one of your reference test jumper cables in both directions using the single-ended loss test to make sure they are all good. If your power meter has internal memory to record data be sure you know how to use this also. You can often customize these reports to your specific needs - figure all this out before you go it the field - it could save you time and on installations, time is money!

#### 3. Know the network you're testing...

This is an important part of the documentation process we discussed earlier. Make sure you have cable layouts for every fiber you have to test. Prepare a spreadsheet of all the cables and fibers before you go in the field and print a copy for recording your test data. You may record all your test data either by hand or if your meter has a memory feature, it will keep test results in on-board memory that can be printed or transferred to a computer when you return to the office.

### A note on using a fiber optic source eye safety...

Fiber optic sources, including test equipment, are generally too low in power to cause any eye damage, but it's still a good idea to check connectors with a power meter before looking into it. Some telco DWDM and CATV systems have very high power and they could be harmful, so better safe than sorry.

Fiber optic testing includes three basic tests that we will cover separately: Visual inspection for continuity or connector checking, Loss testing, and Network Testing.

### Visual Inspection

#### Visual Tracing

Continuity checking makes certain the fibers are not broken and to trace a path of a fiber from one end to another through many connections. Use a visible light "fiber optic tracer" or "pocket visual fault locator". It looks like a flashlight or a pen-like instrument with a lightbulb or LED soure that mates to a fiber optic connector. Attach a cable to test to the visual tracer and look at the other end to see the light transmitted through the core of the fiber. If there is no light at the end, go back to intermediate connections to find the bad section of the cable. 

A good example of how it can save time and money is testing fiber on a reel before you pull it to make sure it hasn't been damaged during shipment. Look for visible signs of damage (like cracked or broken reels, kinks in the cable, etc.) . For testing, visual tracers help also identify the next fiber to be tested for loss with the test kit. When connecting cables at patch panels, use the visual tracer to make sure each connection is the right two fibers! And to make certain the proper fibers are connected to the transmitter and receiver, use the visual tracer in place of the transmitter and your eye instead of the receiver (remember that fiber optic links work in the infrared so you can't see anything anyway.)

#### Visual Fault Location

A higher power version of the tracer uses a laser that can also find faults. The red laser light is powerful enough to show breaks in fibers or high loss connectors. You can actually see the loss of the bright red light even through many yellow or orange simplex cable jackets except black or gray jackets. You can also use this gadget to optimize mechanical splices or prepolished-splice type fiber optic connectors. In fact- don't even think of doing one of those connectors without one  no other method will assure you of high yield with them.

#### Visual Connector Inspection

Fiber optic microscopes are used to inspect connectors to check the quality of the termination procedure and diagnose problems. A well made connector will have a smooth , polished, scratch free finish and the fiber will not show any signs of cracks, chips or areas where the fiber is either protruding from the end of the ferrule or pulling back into it. 

The magnification for viewing connectors can be 30 to 400 power but it is best to use a medium magnification. The best microscopes allow you to inspect the connector from several angles, either by tilting the connector or having angle illumination to get the best picture of what's going on. Check to make sure the microscope has an easy-to-use adapter to attach the connectors of interest to the microscope. 

And remember to check that no power is present in the cable before you look at it in a microscope  protect your eyes!

### Optical Power - Power or Loss? ("Absolute" vs. "Relative")

Practically every measurement in fiber optics refers to optical power. The power output of a transmitter or the input to receiver are "absolute" optical power measurements, that is, you measure the actual value of the power. Loss is a "relative" power measurement, the difference between the power coupled into a component like a cable or a connector and the power that is transmitted through it. This difference is what we call optical loss and defines the performance of a cable, connector, splice, etc.

### Measuring power

Power in a fiber optic system is like voltage in an electrical circuit - it's what makes things happen! It's important to have enough power, but not too much. Too little power and the receiver may not be able to distinguish the signal from noise; too much power overloads the receiver and causes errors too. 

Measuring power requires only a power meter (most come with a screw-on adapter that matches the connector being tested) and a little help from the network electronics to turn on the transmitter. Remember when you measure power, the meter must be set to the proper range (usually dBm, sometimes microwatts, but never "dB"  that's a relative power range used only for testing loss!) and the proper wavelengths  matching the source being used. Refer to the instructions that come with the test equipment for setup and measurement instructions (and don't wait until you get to the job site to try the equipment)! 

To measure power, attach the meter to the cable that has the output you want to measure. That can be at the receiver to measure receiver power, or to a reference test cable (tested and known to be good) that is attached to the transmitter, acting as the "source", to measure transmitter power. Turn on the transmitter/source and note the power the meter measures. Compare it to the specified power for the system and make sure it's enough power but not too much.

### Testing loss

Loss testing is the difference between the power coupled into the cable at the transmitter end and what comes out at the receiver end. Testing for loss requires measuring the optical power lost in a cable (including connectors ,splices, etc.) with a fiber optic source and power meter by mating the cable being tested to known good reference cable. 

In addition to our power meter, we will need a test source. The test source should match the type of source (LED or laser) and wavelength (850, 1300, 1550 nm). Again, read the instructions that come with the unit carefully. 

We also need one or two reference cables, depending on the test we wish to perform. The accuracy of the measurement we make will depend on the quality of your reference cables. Always test your reference cables by the single ended method shown below to make sure they're good before you start testing other cables! 

Next we need to set our reference power for loss  our "0 dB" value. Correct setting of the launch power is critical to making good loss measurements!

### Clean your connectors and set up your equipment like this:

Turn on the source and select the wavelength you want for the loss test. Turn on the meter, select the "dBm" or "dB" range and select the wavelength you want for the loss test. Measure the power at the meter. This is your reference power level for all loss measurements. If your meter has a "zero" function, set this as your "0" reference. 

Some reference books and manuals show setting the reference power for loss using both a launch and receive cable mated with a mating adapter. This method is acceptable for some tests, but will reduce the loss you measure by the amount of loss between your reference cables when you set your "0dB loss" reference. Also, if either the launch or receive cable is bad, setting the reference with both cables hides the fact. Then you could begin testing with bad launch cables making all your loss measurements wrong. EIA/TIA 568 calls for a single cable reference, while OFSTP-14 allows either method.

### Testing Loss

There are two methods that are used to measure loss, which we call "single-ended loss" and "double-ended loss". Single-ended loss uses only the launch cable, while double-ended loss uses a receive cable attached to the meter also. 

Single-ended loss is measured by mating the cable you want to test to the reference launch cable and measuring the power out the far end with the meter. When you do this you measure 1. the loss of the connector mated to the launch cable and 2. the loss of any fiber, splices or other connectors in the cable you are testing. This method is described in FOTP-171 and is shown in the drawing. Reverse the cable to test the connector on the other end. 

In a double-ended loss test, you attach the cable to test between two reference cables, one attached to the source and one to the meter. This way, you measure two connectors' loses, one on each end, plus the loss of all the cable or cables in between. This is the method specified in OFSTP-14, the test for loss in an installed cable plant.

### What Loss Should You Get When Testing Cables?

While it is difficult to generalize, here are some guidelines: 

- For each connector, figure 0.5 dB loss (0.7 max)
- For each splice, figure 0.2 dB
- For multimode fiber, the loss is about 3 dB per km for 850 nm sources, 1 dB per km for 1300 nm. This roughly translates into a loss of 0.1 dB per 100 feet for 850 nm, 0.1 dB per 300 feet for 1300 nm.
- For singlemode fiber, the loss is about 0.5 dB per km for 1300 nm sources, 0.4 dB per km for 1550 nm. 

This roughly translates into a loss of 0.1 dB per 600 feet for 1300 nm, 0.1 dB per 750 feet for 1300 nm. So for the loss of a cable plant, calculate the approximate loss as: 

(0.5 dB X # connectors) + (0.2 dB x # splices) + fiber loss on the total length of cable

### Troubleshooting Hints:

If you have high loss in a cable, make sure to reverse it and test in the opposite direction using the single-ended method. Since the single ended test only tests the connector on one end, you can isolate a bad connector - it's the one at the launch cable end (mated to the launch cable) on the test when you measure high loss. 

High loss in the double ended test should be isolated by retesting single-ended and reversing the direction of test to see if the end connector is bad. If the loss is the same, you need to either test each segment separately to isolate the bad segment or, if it is long enough, use an OTDR. 

If you see no light through the cable (very high loss - only darkness when tested with your visual tracer), it's probably one of the connectors, and you have few options. The best one is to isolate the problem cable, cut the connector of one end (flip a coin to choose) and hope it was the bad one (well, you have a 50-50 chance!)

### OTDR Testing

As we mentioned earlier, OTDRs are always used on OSP cables to verify the loss of each splice. But they are also used as troubleshooting tools. Let's look at how an OTDR works and see how it can help testing and troubleshooting.

### How OTDRs Work

Unlike sources and power meters which measure the loss of the fiber optic cable plant directly, the OTDR works indirectly. The source and meter duplicate the transmitter and receiver of the fiber optic transmission link, so the measurement correlates well with actual system loss. 

The OTDR, however, uses backscattered light of the fiber to imply loss. The OTDR works like RADAR, sending a high power laser light pulse down the fiber and looking for return signals from backscattered light in the fiber itself or reflected light from connector or splice interfaces. 

At any point in time, the light the OTDR sees is the light scattered from the pulse passing through a region of the fiber. Only a small amount of light is scattered back toward the OTDR, but with sensitive receivers and signal averaging, it is possible to make measurements over relatively long distances. Since it is possible to calibrate the speed of the pulse as it passes down the fiber, the OTDR can measure time, calculate the pulse position in the fiber and correlate what it sees in backscattered light with an actual location in the fiber. Thus it can create a display of the amount of backscattered light at any point in the fiber. 

Since the pulse is attenuated in the fiber as it passes along the fiber and suffers loss in connectors and splices, the amount of power in the test pulse decreases as it passes along the fiber in the cable plant under test. Thus the portion of the light being backscattered will be reduced accordingly, producing a picture of the actual loss occurring in the fiber. Some calculations are necessary to convert this information into a display, since the process occurs twice, once going out from the OTDR and once on the return path from the scattering at the test pulse.

There is a lot of information in an OTDR display. The slope of the fiber trace shows the attenuation coefficient of the fiber and is calibrated in dB/km by the OTDR. In order to measure fiber attenuation, you need a fairly long length of fiber with no distortions on either end from the OTDR resolution or overloading due to large reflections. If the fiber looks nonlinear at either end, especially near a reflective event like a connector, avoid that section when measuring loss. 

Connectors and splices are called "events" in OTDR jargon. Both should show a loss, but connectors and mechanical splices will also show a reflective peak so you can distinguish them from fusion splices. Also, the height of that peak will indicate the amount of reflection at the event, unless it is so large that it saturates the OTDR receiver. Then peak will have a flat top and tail on the far end, indicating the receiver was overloaded. The width of the peak shows the distance resolution of the OTDR, or how close it can detect events.

OTDRs can also detect problems in the cable caused during installation. If a fiber is broken, it will show up as the end of the fiber much shorter than the cable or a high loss splice at the wrong place. If excessive stress is placed on the cable due to kinking or too tight a bend radius, it will look like a splice at the wrong location.

### OTDR Limitations

The limited distance resolution of the OTDR makes it very hard to use in a LAN or building environment where cables are usually only a few hundred meters long. The OTDR has a great deal of difficulty resolving features in the short cables of a LAN and is likely to show "ghosts" from reflections at connectors, more often than not simply confusing the user.

### Using The OTDR

When using an OTDR, there are a few cautions that will make testing easier and more understandable. First always use a long launch cable, which allows the OTDR to settle down after the initial pulse and provides a reference cable for testing the first connector on the cable. Always start with the OTDR set for the shortest pulse width for best resolution and a range at least 2 times the length of the cable you are testing. Make an initial trace and see how you need to change the parameters to get better results. 

Coming soon - our OTDR self-study course will teach you a lot more about how to use OTDRs!

### Restoration

The time may come when you have to troubleshoot and fix the cable plant. If you have a critical application or lots of network cable, you should be ready to do it yourself. Smaller networks can rely on a contractor. If you plan to do it yourself, you need to have equipment ready (extra cables, mechanical splices, quick termination connectors, etc., plus test equipment.) and someone who knows how to use it. 

We cannot emphasize more strongly the need to have good documentation on the cable plant. If you don't know where the cables go, how long they are or what they tested for loss, you will be spinning you wheels from the get-go. And you need tools to diagnose problems and fix them, and spares including a fusion splicer or some mechanical splices and spare cables. In fact, when you install cable, save the leftovers for restoration! And the first thing you must decide is if the problem is with the cables or the equipment using it. A simple power meter can test sources for output and receivers for input and a visual tracer will check for fiber continuity. If the problem is in the cable plant, the OTDR is the next tool needed to locate the fault.